# GUV-CFD Simulation Report

Illuminate room design file: C:\Users\hukcl\Documents\1work\222\Collaboration projects\South Africa\TB project\simulation files\patient ward 4B1 v4.guv

CFD Project file: n/a

OpenFoam directory: \\wsl.localhost\Ubuntu\home\hclaus\OpenFOAM\hclaus-v2412\run\patient_ward_4B1_v11_simdecay1_w_ftest

| Simulation date | 2026-08-01 10:16 |
| --- | --- |
| Total elapsed time | 1h 16m 39s |
| CPU | 12th Gen Intel(R) Core(TM) i7-1255U |
| RAM | 15.7 GB |
| GPU | Intel(R) Iris(R) Xe Graphics (not used - this simulation's OpenFOAM solve is CPU-only) |

## Room Setup

| Room dimensions | 3.2 x 4.8 x 2.57 meters |
| --- | --- |
| Lamps | 4 |
| Ventilation ACH | 3 /hr |
| UV inactivation constant Z | 3 cm²/mJ |
| Inlet | xMin, y=2.4m z=2.4m, size=0.4x0.4m |
| Outlet | xMax, y=2.4m z=0.3m, size=0.4x0.4m |

| Mixing fan | 0.5 m/s, direction=down, position=(1.6, 2.4, 2.3)m, radius=0.6m |
| --- | --- |

## Case Setup

## Convergence & Trust

| Flow field | Accepted via bounded oscillation - never fully converged (common for a jet/fan impinging on a wall or floor; see Advanced Settings > Flow oscillation acceptance) |
| --- | --- |
| Ventilation delivery | 2.9/hr measured vs 3/hr nominal (97%) - OK |

## Results

Note: T is the OpenFOAM field name for the transported scalar this whole simulation tracks - the substance being reduced, per unit volume. In a GUV disinfection context this is typically a pathogen concentration, e.g. CFU/m³ (colony-forming units per cubic meter) or an equivalent airborne-contaminant unit; the CFD itself is unit-agnostic and just tracks relative concentration.

| ### Room Settings |  |
| --- | --- |
| Average fluence rate | 2.869 µW/cm² |
| Susceptibility constant Z (cm² / mJ) | 3.0 |
| Set well-mixed steady-state T (entire volume) | 1 |
| Calculated eACH | 30.99 /hr |
| ### Results from Decay mode analysis |  |
| ACH (air) measured | 2.904 /hr |
| Effective ACHeff CFD measured | 2.316 /hr (95% CI: 2.314–2.318 /hr) |
| ACH efficiency | 79.7% |
| eACHeff CFD measured | 19.82 /hr (95% CI: 19.81–19.84 /hr) |
| Total Room ACHeff+eACHeff | 22.14 /hr |
| ### Analysis of simulations |  |
| Total average Pathogen reduction in room per hour | 89.5% |
| Room pathogen removal efficacy | 65.1% |
| ### UV Germicidal Effectiveness |  |
| True UVGI Effectiveness | 89.5% |

## Monitoring Results

| Patient pathogen reduction | xx.x % |
| --- | --- |
| Exhaust pathogen reduction | xx.x % |

Note: the effective/measured ventilation ACH above is not the airflow rate delivered by the inlet - that's fixed at the nominal design ACH by the boundary condition. It's measured directly by a dedicated UV-off control run (uniform initial concentration, ventilation only, no source) run alongside the main scenario - see the OpenFOAM Notes help page for why this is preferred over deriving it from Phase 1's own point-source buildup. Reads lower than nominal when the room mixes imperfectly (e.g. inlet/outlet short-circuiting on the same wall).

Assuming well mixed condition eACH = Z*Eavg

Mass balance -air in vs. air out – is an indication of how good the model settled

This measures the actual T removal by air, in not well mixed conditions will be different to (lower) that nominal ACH.

Gives an indication how well the air is mixed

The actual eACH value from the CFD run

Based on steady state calculation taking eACHeff and ACHeff into account

= (ACHeff + eACHeff ) / ( ACH + eACH) – shows the real efficiency of the setup (CFD) vs. nominal values of ACH and eACH

This is a value showing the effectiveness of UV over mechanical ventilation alone. See “Miller, Shelly L. / MacHer, Janet M.; Evaluation of a Methodology for Quantifying the Effect of Room Air Ultraviolet Germicidal Irradiation on Airborne Bacteria; 2000-09; Aerosol Science and Technology , Vol. 33, No. 3
Taylor & Francis; p. 283” ; E= 1- (TSS2/TSS1-TSS2) or E= 1-(eACH/(ACHeff+eACH)

Based on steady state calculation