## Results

Note: T is the OpenFOAM field name for the transported scalar this whole simulation tracks - the substance being reduced, per unit volume. In a GUV disinfection context this is typically a pathogen concentration, e.g. CFU/m³ (colony-forming units per cubic meter) or an equivalent airborne-contaminant unit; the CFD itself is unit-agnostic and just tracks relative concentration.

| ### Room Settings |  |
| --- | --- |
| Average fluence rate | 2.869 µW/cm² |
| Susceptibility constant Z (cm² / mJ) | <6> |
| Target well-mixed steady-state T | 1 |
| Calculated Source injection rate Tinj (T-units/s ) | 0.06579 |
| Calculated eACH | 61.98 /hr |
| ### Phase 1 – simulation results (no UV, only mechanical ACH, with source injection) |  |
| Steady state T, calculated from moving average (<15% > of last results) | 2.009 (plateaued) |
| CV (<15% > of last results) | 0.0% |
| Extrapolated TSS1∞ | 2.028, fit CV=0.04% |
| Phase 2 – simulation results (with UV, only mechanical ACH, with source injection) |  |
| Steady State TSS2, calculated from moving average (last <749> iterations) | 0.1161 |
| CV (last <749> iterations) | 0.4% |
| Extrapolated TSS2∞ | 0.1194, fit CV=0.46% |
| ### Analysis of simulations |  |
| Total average Pathogen reduction in room | 94.1% |
| Effective pathogen (mechanical) ACHeff (using extrapolated T∞) | 2.959 /hr |
| Room ventilation pathogen removal efficacy EACHeff | 49.3% |
| True CFD measured eACHCFD | 47.28 /hr |
| Simple CFD measured eACHCFD_s | 95.9% /hr |
| Total ACH in room (ACH+eACH_uv) | 50.24 /hr |
| ### UV Germicidal Effectiveness |  |
| True UVGI Effectiveness | 94.5% |
| Simple UVGI Effectiveness | 94.1% |

Calculated based on given ACH and target well mixed steady state T with equation < Tinj = …>. If more than one injection source is given, the amount is equality divided by the quantity of sources

Assuming well mixed condition eACH = Z*Eavg

CV = Standard deviation/ average

Extrapolated based on <n> simulation points with equation <TSS1∞ = …….>. T is the room average

Extrapolated based on <n> simulation points with equation <TSS2∞ = …….>. T is the room average

Based on average T and sum of mechanical ACH and UV based eACHUsing extrapolated T∞, calculated with equation < reduction = …>

In not well mixed conditions the actual pathogen removal will be different than the mechanical air exchange rate (ACH). This value ACHeff is calculated from the simulated T values over time of phase 1 (no UV) by approximating the data of T(t) to equation <…….>

EACHeff= ACHeff  / ACH

Based on true mechanical ventilation ACHeff (using extrapolated T∞) calculated with equation <eACHCFD =…..>

Based on rated ventilation ACH (and using extrapolated T∞) calculated with equation <eACHCFD_s = eACHCFD /EACHeff>

This is a value showing the effectiveness of UV over mechanical ventilation alone. See “Miller, Shelly L. / MacHer, Janet M.; Evaluation of a Methodology for Quantifying the Effect of Room Air Ultraviolet Germicidal Irradiation on Airborne Bacteria; 2000-09; Aerosol Science and Technology , Vol. 33, No. 3
Taylor & Francis; p. 283” ; E= 1- (TSS2/TSS1-TSS2) or E= 1-(eACH/(ACHeff+eACH)

Instead of using the actual ACHeff (which can be substantially lower than rated ACH), we use ACH; 
E= 1-(eACH/(ACH+eACH)